LaGrange PWS

2019 Drinking Water Consumer Confidence Report (for the 2018 calendar year) Introduction 

The LaGrange PWS has prepared the following report to provide information to you, the consumer, on the quality of our drinking water. Included within this report is general health information, water quality test results, how to participate in decisions concerning your drinking water and water system contacts.

Source Water Information

LaGrange PWS receives its drinking water from Avon Lake Regional Water (Avon Lake City PWS). Avon Lake Regional Water receives its drinking water from Lake Erie. In Avon Lake, there are two separate intakes to ensure our ability to pump from this virtually endless source of quality raw water.

Avon Lake Regional Water treats water to meet EPA drinking water quality standards. A Source Water Assessment Report was prepared for Avon Lake Regional Water by Ohio EPA. Copies of the complete source water assessment report prepared for Avon Lake are available by contacting Greg Yuronich at

(440) 933-3229 or by viewing this webpage.

http://wwwapp.epa.ohio.gov/gis(swpa(OH4700311.pdf

Excerpt from Drinking Water Source Assessment for the City of Avon Lake 6.0 SUSCEPTIBILITY ANALYSIS

For the purposes of source water assessments, all surface waters are considered to be susceptible to contamination. By their nature surface waters are accessible and can be readily contaminated by chemicals and pathogens with relatively short travel times from source to the intake. Based on the information compiled for this assessment, the Avon Lake Water System drinking water source protection area (CAZ) is susceptible to contamination from municipal waste water treatment discharges, industrial waste water discharges, air contamination deposition, combined sewer overflows, runoff from residential, agricultural and urban areas, oil and gas production and transportation, and accidental releases and spills from rail and vehicular traffic as well as from commercial shipping operations and recreational boating.

It is important to note that this assessment is based on available data, and therefore may not reflect current conditions in all cases. Water quality, land uses and other activities that are potential sources of contamination may change with time. While the source water for the City of Avon Lake is considered susceptible to contamination, historically, the Avon Lake Public Water System has effectively treated thiS source water to meet drinking water quality standards.

What are sources of contamination to drinking water?

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, sprlngs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.

Contaminants that may be present in source water include: (A) Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife; (B) Inorganic contaminants, such as salts and metals, which can be naturallyoccurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming; (C) Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses; (D) Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban Strom water runoff, and septic systems; (E) Radioactive contaminants, which can be naturally-occurring or be the result of oil and gas production and mining activities.

In order to ensure that tap water is safe to drink, USEPA prescribes regulations which limit the amount of certain contaminants in water provided by public water systems. FDA regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Federal Environmental Protection Agency's Safe Drinking Water Hotline (1-800-426-4791).

Who needs to take special precautions?

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons, such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infection. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (1-800-426-4791).

Table of Detected Contaminants

Listed below is information on those contaminants that were found in the LaGrange PWS drinking water.

# LaGrange PWS TABLE OF DETECTED CONTAMINANTS 2018

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Contaminants  (Units) | MCI-G | MCL | | Level  Found | | Range of Detections | Violatio n | Sample Year | Typical Source of Contaminants |
| Microbiological Contaminants | | | | | |  |  |  |  |
| Turbidity (NTU)I |  |  | | 0.29 | | 0.04-0.29 | No | 2018 | Soil Runoff |
| Turbidity (% samples meeting standard |  |  | | 100% | | 100% | No | 2018 | Soil Runoff |
| Total Organic  Carbon (TOC)2 |  |  | | 1.38 | | 1.22-1.86 | No | 2017-18 | Naturally present in the environment |
| Disinfectants and Disinfection Byproducts3 | | | | | |  |  |  |  |
| Total Chlorine (ppm) | MCLG = 4 | MRDL | | 1.2 | | 1.0-1.4 | No | 2017-18 | Water additive used to control microbes |
| Haloacetic Acids (HAA5) (ppb)4 |  | 60 | | 24.7 | | 8.0-38.4 | No | 2017-18 | By-product of drinking water disinfection |
| Total  Trihalomethanes  TTHM b 4 |  | 80 | | 58.9 | | 27.3-70.0 | No | 2017-18 | By-product of drinking water disinfection |
| Inorganic Contaminants | | | | | |  |  |  |  |
| Barium (ppm) | 2 | 2 | | 0.028 | | 0.028 | No | 2018 | Discharge of drilling wastes; Discharge from metal refineries; Erosion of natural de osits |
| Fluoride (ppm) | 4 | 4 | | 1 | | 1.2 | No | 2018 | Erosion of natural deposits; Water additive which promotes strong teeth; Discharge from fertilizer and aluminum factories |
| Nitrate (ppm) | 10 | 10 | | 1.4 | | O. 1-1.4 | No | 2018 | Run off from fertilizer use,  Leaching from septic tanks, seweage;  Erosion of natural de osits |
| Lead and Copper | | | | | | | | | |
|  | Actlon  Level (AL) | | Individua  Results over the  AL | | 90% of test levels were less than | | Violatio n | Year  Sampled | Typical source of Contaminants |
| Lead (ppb) | 15 ppb | |  | | <3.o | | No | 1st Half  2018 | Corosion of household plumbing systems; erosion of natural de osits |
| Zero out of 20 samples were found to have lead levels in excess of the lead actlm level of 15 | | | | | | | | |
| Lead (ppb) | 15 ppb | |  | |  | | No | 2nd Half  2018 | Corosion of household plumbing systems; erosion of natural deposits |
| Zero out of 20 samples were found to have lead levels In excess of the lead actlon level of 15 b. | | | | | | | | |
| Copper (ppm) | 1.3 ppm | |  | | 0.064 | | No | 1st Half  2018 | Erosions of natural deposits; leaching from wood preservatives; Corrosions of household plumbing s stems |
| Zero out of 20 samples were found to have copper lwels In excess of the copper action level of 1.3 | | | | | | | | |
| Copper (ppm) | 1.3 ppm | |  | | 0.065 | | No | 2nd Half  2018 | Erosions of natural deposits; leaching from wood preservatives; Corrosions of household plumbing s stems |
| Zero out of 20 samples were found to have copper levels In excess of the copper action level of 1.3 | | | | | | | | |

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. LaGrange PWS is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 secorfls to 2 minutes before using water for drinking or cooking. If you are concemed about lead in your water, you may wish to have your water tested. Infonnation on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline at 800-426-4791 or at http://www.epa.gov/safewaternead.

LaGrange has a current, unconditioned license to operate our water system from the Ohio EPA.

Turbidity is a measure of the cloudiness of water and is an indication of the effectiveness of our filtration system. The turbidity limit set by the EPA is 0.3 NTU in 95% of the samples analyzed each month and shall not exceed I NTU at any time. As reported above the Avon Lake WTP highest recorded turbidity result for 2018 was 0.29 NTU and lowest monthly perentage of samples meeting the turbidity limits was 100%.

2 The value reported under "Level Found" for Total Organic Carbon (TOC) is the lowest ratio between percentage of TOC actually removed to the percentage of

TOC required to be removed. This removal ratio is calculated as the ratio between the actual TOC removal ard the TOC rule removal requirer1Ents and other parameters. A value of at least one (l) indicates that the water system is in compliance with TOC removal requirements.

3These contaminants level found is the highest compliance value based on a running annual average. This average includes results from 2017 & 2018.

Ü Disinfection byproducts are the result of providing continuous disinfection of your drinking water and form when disinfectants combine with organic matter naturally occurring in the source water. Disinfection byproducts are grouped into two categories, Total Trihalomethanes (TTHM) and

Haloacetic Acids (HAAS). USEPA sets standards for controlling the levels of disinfectants and disinfectant byproducts in drinking water, including both


TTHMs and HAA5s."

DEFINITIONS

l. Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

2. Contaminant: Any physical, chemical, biological, or radiological substance or matter in water. 3. Maximum Contaminant Level (MCL): The highest level of contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology. 4. Maximum Contaminant Level Goal (MCLG): The level of contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety.

1. Maximum Residual Disinfectant Level (MRDL): The highest residual disinfectant level allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.
2. Maximum Residual Disinfectant Level Goal (MRDLG): The level of residual disinfectant below which there is no known or expected risk to health. MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.
3. NA: Not Applicable
4. ND: Not Detected
5. NTU: Nephelometric Turbidity Units
6. Parts per billion (ppb) or Micrograms per Liter (ug/L) are of measure for concentration of a contaminant. A part per billion corresponds to one second in 31.7 years.
7. Parts per million (ppm) or Milligrams per Liter (mg/L) are of measure for concentration of a contaminant. A part per million corresponds to one second in a little over 1 1.5 days.
8. Total Organic Carbon (TOC) has no health effects. However, TOC provides a medium when the water is disinfected for the formation of disinfection byproducts. TOC removal early in the treatment plant is required.
9. Treatment Technique (TD: A required process intended to reduce the level of a contaminant in drinking water. For example Avon Lake Regional Water adds lime to increase the pH of our finished water in order to maintain compliance with the lead and copper rule.
10. VOC: Volatile Organic Chemicals
11. WTP:WaterTreatmentP1ant
12. The "<" Symbol: A symbol that means less than. A result of <5 means that the lowest level that could be detected was 5 and the contaminant in that sample was not detected.

 Unregulated Year

Contaminants Sample

Unregulated contaminants are those for which EPA has not established drinking water standards. The purpose of unregulated contaminant monitoring is to assist EPA in determining the occurrence of unregulated contaminants in drinking water and whether future regulation is warranted. In 2018 Avon Lake Regional Water participated in the fourth round of the Unregulated Contaminant Monitoring Rule (UCMR 4). For a copy of the results please call Greg Yuronich at 440-933-3229.

Turbidity

Turbidity is a measure of the cloudiness of water and is an indication of the effectiveness of our filtration system. The turbidity limit set by the EPA is 0.3 NTU in 95% ofthe samples analyzed each month and shail not exceed 1 NTU at any time. As reported above, Avon Lake Regional Water's highest recorded turbidity result for 2018 was 0.29 NTU and lowest monthly percentage of samples meeting the turbidity limits was 100%.

Lead Educational Information

If present, elevated levels of iead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. LaGrange PWS is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline at 800426-47910r at http://www.epa.gov(safewater/lead.

License to Operate (LTO) Status Information

In 2018 we had an unconditioned license to operate our water system.

Public Particlpation and Contact Information

How do I participate in decisions concerning my drinking water?

Public participation and comment are encouraged at regular meetings of the LaGrange Village Council which meets the second and fourth Tuesday of every month at 7:00PM at the Lagrange Village Town Hall 301 Liberty Street, LaGrange, Ohio 44050. For more information on your drinking water contact Robert Hulec, Superintendent, or Walt Sukey, Village Administrator at 440-355-6045.